## DiscreteAlarms
F ¦ Emergency push button 1 ¦ 513S1ESTOP1 | Errors | wHMI_Fault1 | 0
F ¦ Emergency push button 2 External ¦ 513S2ESTOP2 | Errors | wHMI_Fault1 | 1
F ¦ Emergency stop from Fire detection ¦ 081K3 | Errors | wHMI_Fault1 | 2
F ¦ Spare | Errors | wHMI_Fault1 | 3
F ¦ MAPA 400V surge suppressor trip ¦ 001F1 | Errors | wHMI_Fault1 | 4
F ¦ MAPA 230V UPS surge suppressor trip ¦ 101F2 | Errors | wHMI_Fault1 | 5
F ¦ Spare | Errors | wHMI_Fault1 | 6
F ¦ Power supply 24Vdc Ethernet Switch open ¦ XSG3 | Errors | wHMI_Fault1 | 7
F ¦ Power supply 24Vdc Safety PLC board open ¦ XSG4 | Errors | wHMI_Fault1 | 8
F ¦ Spare | Errors | wHMI_Fault1 | 9
F ¦ Spare | Errors | wHMI_Fault1 | 10
F ¦ Fire fighting system Gas Release ¦ 081K2 | Errors | wHMI_Fault1 | 11
F ¦ Spare | Errors | wHMI_Fault1 | 12
F ¦ Profisave receive from PH2HD Fault | Errors | wHMI_Fault1 | 13
F ¦ Power supply UPS shunt opening release ¦ 111F1 | Errors | wHMI_Fault1 | 14
F¦ Emergency State | Errors | wHMI_Fault1 | 15
F ¦ Profinet PH2HD Fault | Errors | wHMI_Fault2 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 1
F ¦ Spare | Errors | wHMI_Fault2 | 2
F ¦ Spare | Errors | wHMI_Fault2 | 3
F ¦ Spare | Errors | wHMI_Fault2 | 4
F ¦ Spare | Errors | wHMI_Fault2 | 5
F ¦ Spare | Errors | wHMI_Fault2 | 6
F ¦ Spare | Errors | wHMI_Fault2 | 7
F ¦ E-Stop System BMS1 | Errors | wHMI_Fault2 | 8
F ¦ E-Stop System BMS2 | Errors | wHMI_Fault2 | 9
F ¦ Spare | Errors | wHMI_Fault2 | 10
F ¦ Spare | Errors | wHMI_Fault2 | 11
F ¦ Spare | Errors | wHMI_Fault2 | 12
F ¦ Spare | Errors | wHMI_Fault2 | 13
F ¦ Spare | Errors | wHMI_Fault2 | 14
F ¦ Spare | Errors | wHMI_Fault2 | 15
A ¦ Main circuit breaker 400V ¦ 003F1 | Errors | wHMI_Alarm1 | 0
A ¦ Voltage Measurement Protection Socomec ¦ 003F2 | Errors | wHMI_Alarm1 | 1
A ¦ Power Supply HVAC 1.1 ¦ 13F1 | Errors | wHMI_Alarm1 | 2
A ¦ Power Supply HVAC 1.2 ¦ 13F2 | Errors | wHMI_Alarm1 | 3
A ¦ Power Supply HVAC 1.3 ¦ 13F3 | Errors | wHMI_Alarm1 | 4
A ¦ Power Supply HVAC 1.4 ¦ 15F1 | Errors | wHMI_Alarm1 | 5
A ¦ Power Supply HVAC 1.5 ¦ 15F2 | Errors | wHMI_Alarm1 | 6
A ¦ Power Supply HVAC 2.1 ¦ 15F3 | Errors | wHMI_Alarm1 | 7
A ¦ Power Supply HVAC 2.2 ¦ 17F1 | Errors | wHMI_Alarm1 | 8
A ¦ Power Supply HVAC 2.3 ¦ 17F2 | Errors | wHMI_Alarm1 | 9
A ¦ Power Supply HVAC 2.4 ¦ 17F3 | Errors | wHMI_Alarm1 | 10
A ¦ Power Supply HVAC 2.5 ¦ 19F1 | Errors | wHMI_Alarm1 | 11
A ¦ Power Supply Fire Fighting System ¦ 19F2 | Errors | wHMI_Alarm1 | 12
A ¦ MAPA Main Circuit Breaker 400V | Errors | wHMI_Alarm1 | 13
A ¦ Spare | Errors | wHMI_Alarm1 | 14
A ¦ Fire detection general fault ¦ 081K1 | Errors | wHMI_Alarm1 | 15
A ¦ Power Supply UPS PAC 3220¦ 113F1 | Errors | wHMI_Alarm2 | 0
A ¦ Power Supply BB1 Control Aux1 open ¦ 103F1+103F2 | Errors | wHMI_Alarm2 | 1
A ¦ Power Supply BB1 Control Aux2 open ¦ 103F3+103F4 | Errors | wHMI_Alarm2 | 2
A ¦ Power Supply BB2 Control Aux1 open ¦ 105F1+105F2 | Errors | wHMI_Alarm2 | 3
A ¦ Power Supply BB2 Control Aux2 open ¦ 105F4+105F4 | Errors | wHMI_Alarm2 | 4
A ¦ Power Supply PS Unit 1 230Vac/24Vdc ¦ 109F1+109F2 | Errors | wHMI_Alarm2 | 5
A ¦ Power Supply PS Unit 2 230Vac/24Vdc ¦ 109F3+109F4 | Errors | wHMI_Alarm2 | 6
A ¦ Power supply 24Vdc Humidity and Temperature open¦ XSG5 | Errors | wHMI_Alarm2 | 7
A ¦ Power supply 24Vdc PLC IO internal open ¦ XSG8 | Errors | wHMI_Alarm2 | 8
A ¦ Power supply 24Vdc PLC IO external open ¦ XSG9 | Errors | wHMI_Alarm2 | 9
A ¦ Power supply 24Vdc mini PC open ¦ XSG10 | Errors | wHMI_Alarm2 | 10
A ¦ Spare | Errors | wHMI_Alarm2 | 11
A ¦ Disconnector open ¦PWC001-A | Errors | wHMI_Alarm2 | 12
A ¦ Disconnector open ¦PWC001-B | Errors | wHMI_Alarm2 | 13
A ¦ Surge Suppressor Fuse Status ¦PWC001-A | Errors | wHMI_Alarm2 | 14
A ¦ Surge Suppressor Fuse Status ¦PWC001-B | Errors | wHMI_Alarm2 | 15
A ¦ Door opened HVAC 1_1¦535S1 | Errors | wHMI_Alarm3 | 0
A ¦ Door opened HVAC 1_2¦535S2 | Errors | wHMI_Alarm3 | 1
A ¦ Door opened HVAC 1_3¦535S3 | Errors | wHMI_Alarm3 | 2
A ¦ Door opened HVAC 1_4¦535S4 | Errors | wHMI_Alarm3 | 3
A ¦ Door opened HVAC 1_5¦535S5 | Errors | wHMI_Alarm3 | 4
A ¦ Door opened HVAC 2_1¦535S6 | Errors | wHMI_Alarm3 | 5
A ¦ Door opened HVAC 2_2¦537S1 | Errors | wHMI_Alarm3 | 6
A ¦ Door opened HVAC 2_3¦537S2 | Errors | wHMI_Alarm3 | 7
A ¦ Door opened HVAC 2_4¦537S3 | Errors | wHMI_Alarm3 | 8
A ¦ Door opened HVAC 2_5¦537S4 | Errors | wHMI_Alarm3 | 9
A ¦ Spare | Errors | wHMI_Alarm3 | 10
A ¦ Spare | Errors | wHMI_Alarm3 | 11
A ¦ State Machine 1 in Alarm | Errors | wHMI_Alarm3 | 12
A ¦ State Machine 2 in Alarm | Errors | wHMI_Alarm3 | 13
A ¦ Battery room high average temperature | Errors | wHMI_Alarm3 | 14
A ¦ Battery room high single temperature | Errors | wHMI_Alarm3 | 15
A ¦ HVAC1_1 Modbus RTU communication error | Errors | wHMI_Alarm4 | 0
A ¦ HVAC1_2 Modbus RTU communication error | Errors | wHMI_Alarm4 | 1
A ¦ HVAC1_3 Modbus RTU communication error | Errors | wHMI_Alarm4 | 2
A ¦ HVAC1_4 Modbus RTU communication error | Errors | wHMI_Alarm4 | 3
A ¦ HVAC1_5 Modbus RTU communication error | Errors | wHMI_Alarm4 | 4
A ¦ HVAC2_1 Modbus RTU communication error | Errors | wHMI_Alarm4 | 5
A ¦ HVAC2_2 Modbus RTU communication error | Errors | wHMI_Alarm4 | 6
A ¦ HVAC2_3 Modbus RTU communication error | Errors | wHMI_Alarm4 | 7
A ¦ HVAC2_4 Modbus RTU communication error | Errors | wHMI_Alarm4 | 8
A ¦ HVAC2_5 Modbus RTU communication error | Errors | wHMI_Alarm4 | 9
A ¦ Spare | Errors | wHMI_Alarm4 | 10
A ¦ Spare | Errors | wHMI_Alarm4 | 11
A ¦ Spare | Errors | wHMI_Alarm4 | 12
A ¦ Socomec Modbus communication error | Errors | wHMI_Alarm4 | 13
A ¦ BMS1 Modbus TCP communication error | Errors | wHMI_Alarm4 | 14
A ¦ BMS2 Modbus TCP communication error | Errors | wHMI_Alarm4 | 15
W ¦ PWC room sensor high temperature ¦ 561B1 | Warnings | wHMI_Warning1 | 0
W ¦ PWC room sensor low temperature ¦ 561B1 | Warnings | wHMI_Warning1 | 1
W ¦ PWC room sensor temperature read fail ¦ 561B1 | Warnings | wHMI_Warning1 | 2
W ¦ PWC room sensor high humidity ¦ 561B1 | Warnings | wHMI_Warning1 | 3
W ¦ PWC room sensor low humidity ¦ 561B1 | Warnings | wHMI_Warning1 | 4
W ¦ PWC room sensor humidity read fail ¦ 561B1 | Warnings | wHMI_Warning1 | 5
W ¦ PEMS room sensor high temperature ¦ 561B2 | Warnings | wHMI_Warning1 | 6
W ¦ PEMS room sensor low temperature ¦ 561B2 | Warnings | wHMI_Warning1 | 7
W ¦ PEMS room sensor temperature read fail ¦ 561B2 | Warnings | wHMI_Warning1 | 8
W ¦ PEMS room sensor high humidity ¦ 561B2 | Warnings | wHMI_Warning1 | 9
W ¦ PEMS room sensor low humidity ¦ 561B2 | Warnings | wHMI_Warning1 | 10
W ¦ PEMS room sensor humidity read fail ¦ 561B2 | Warnings | wHMI_Warning1 | 11
W ¦ Spare | Warnings | wHMI_Warning1 | 12
W ¦ Spare | Warnings | wHMI_Warning1 | 13
W ¦ Spare | Warnings | wHMI_Warning1 | 14
W ¦ Spare | Warnings | wHMI_Warning1 | 15
W ¦ HVAC General Alarm ¦ HVAC1_1 | Warnings | wHMI_Warning2 | 0
W ¦ HVAC General Alarm ¦ HVAC1_2 | Warnings | wHMI_Warning2 | 1
W ¦ HVAC General Alarm ¦ HVAC1_3 | Warnings | wHMI_Warning2 | 2
W ¦ HVAC General Alarm ¦ HVAC1_4 | Warnings | wHMI_Warning2 | 3
W ¦ HVAC General Alarm ¦ HVAC1_5 | Warnings | wHMI_Warning2 | 4
W ¦ HVAC General Alarm ¦ HVAC2_1 | Warnings | wHMI_Warning2 | 5
W ¦ HVAC General Alarm ¦ HVAC2_2 | Warnings | wHMI_Warning2 | 6
W ¦ HVAC General Alarm ¦ HVAC2_3 | Warnings | wHMI_Warning2 | 7
W ¦ HVAC General Alarm ¦ HVAC2_4 | Warnings | wHMI_Warning2 | 8
W ¦ HVAC General Alarm ¦ HVAC2_5 | Warnings | wHMI_Warning2 | 9
W ¦ Spare | Warnings | wHMI_Warning2 | 10
W ¦ Spare | Warnings | wHMI_Warning2 | 11
W ¦ Spare | Warnings | wHMI_Warning2 | 12
W ¦ Spare | Warnings | wHMI_Warning2 | 13
W ¦ Spare | Warnings | wHMI_Warning2 | 14
W ¦ Spare | Warnings | wHMI_Warning2 | 15
A ¦ Door opened PEMS¦537S5 | Warnings | wHMI_Warning3 | 0
A ¦ Door opened PWC¦537S6 | Warnings | wHMI_Warning3 | 1
W ¦ Spare | Warnings | wHMI_Warning3 | 2
W ¦ Spare | Warnings | wHMI_Warning3 | 3
W ¦ Spare | Warnings | wHMI_Warning3 | 4
W ¦ Spare | Warnings | wHMI_Warning3 | 5
W ¦ Spare | Warnings | wHMI_Warning3 | 6
W ¦ Spare | Warnings | wHMI_Warning3 | 7
W ¦ Spare | Warnings | wHMI_Warning3 | 8
W ¦ Spare | Warnings | wHMI_Warning3 | 9
W ¦ Spare | Warnings | wHMI_Warning3 | 10
W ¦ Spare | Warnings | wHMI_Warning3 | 11
W ¦ Spare | Warnings | wHMI_Warning3 | 12
W ¦ Spare | Warnings | wHMI_Warning3 | 13
W ¦ Spare | Warnings | wHMI_Warning3 | 14
W ¦ Spare | Warnings | wHMI_Warning3 | 15
W ¦ PT100 high temperature ¦ 571B1 | Warnings | wHMI_Warning4 | 0
W ¦ PT100 high temperature ¦ 571B2 | Warnings | wHMI_Warning4 | 1
W ¦ PT100 high temperature ¦ 571B3 | Warnings | wHMI_Warning4 | 2
W ¦ PT100 high temperature ¦ 571B4 | Warnings | wHMI_Warning4 | 3
W ¦ PT100 high temperature ¦ 573B1 | Warnings | wHMI_Warning4 | 4
W ¦ PT100 high temperature ¦ 573B2 | Warnings | wHMI_Warning4 | 5
W ¦ PT100 high temperature ¦ 573B3 | Warnings | wHMI_Warning4 | 6
W ¦ PT100 high temperature ¦ 573B4 | Warnings | wHMI_Warning4 | 7
W ¦ PT100 high temperature ¦ 575B1 | Warnings | wHMI_Warning4 | 8
W ¦ PT100 high temperature ¦ 575B2 | Warnings | wHMI_Warning4 | 9
W ¦ PT100 read fail ¦ 571B1 | Warnings | wHMI_Warning4 | 10
W ¦ PT100 read fail ¦ 571B2 | Warnings | wHMI_Warning4 | 11
W ¦ PT100 read fail ¦ 571B3 | Warnings | wHMI_Warning4 | 12
W ¦ PT100 read fail ¦ 571B4 | Warnings | wHMI_Warning4 | 13
W ¦ PT100 read fail ¦ 573B1 | Warnings | wHMI_Warning4 | 14
W ¦ Spare | Warnings | wHMI_Warning4 | 15
W ¦ PT100 low temperature ¦ 571B1 | Warnings | wHMI_Warning5 | 0
W ¦ PT100 low temperature ¦ 571B2 | Warnings | wHMI_Warning5 | 1
W ¦ PT100 low temperature ¦ 571B3 | Warnings | wHMI_Warning5 | 2
W ¦ PT100 low temperature ¦ 571B4 | Warnings | wHMI_Warning5 | 3
W ¦ PT100 low temperature ¦ 573B1 | Warnings | wHMI_Warning5 | 4
W ¦ PT100 low temperature ¦ 573B2 | Warnings | wHMI_Warning5 | 5
W ¦ PT100 low temperature ¦ 573B3 | Warnings | wHMI_Warning5 | 6
W ¦ PT100 low temperature ¦ 573B4 | Warnings | wHMI_Warning5 | 7
W ¦ PT100 low temperature ¦ 575B1 | Warnings | wHMI_Warning5 | 8
W ¦ PT100 low temperature ¦ 575B2 | Warnings | wHMI_Warning5 | 9
W ¦ PT100 read fail ¦ 573B2 | Warnings | wHMI_Warning5 | 10
W ¦ PT100 read fail ¦ 573B3 | Warnings | wHMI_Warning5 | 11
W ¦ PT100 read fail ¦ 573B4 | Warnings | wHMI_Warning5 | 12
W ¦ PT100 read fail ¦ 575B1 | Warnings | wHMI_Warning5 | 13
W ¦ PT100 read fail ¦ 575B2 | Warnings | wHMI_Warning5 | 14
| Warnings | wHMI_Warning5 | 15